DOOR HARDWARE

SECTION 08 71 00

GENERAL

GENERAL PROVISIONS

Attention is directed to the CONTRACT AND GENERAL CONDITIONS and all Sections within DIVISION 01 - GENERAL REQUIREMENTS which are hereby made a part of this Section of the Specifications.

DESCRIPTION OF WORK

Work Included:  Provide labor, materials and equipment necessary to complete the work of this Section, including but not limited to the following:

Commercial door hardware.

Cylinders for doors specified in other Sections as listed below.

Alternates: Not Applicable.

Items To Be Installed Only: Not Applicable.

Items To Be Furnished Only:  Furnish the following items for installation by the designated Sections: Not Applicable

Related Work: The following items are not included in this Section and will be performed under the designated Sections:

Section 08 11 13 - HOLLOW METAL Doors and Frames for standard doors and fire rated doors.

Section 08 14 16 - FLUSH Wood Doors for standard doors and fire rated doors.

SUBMITTALS

Product Data:  Include installation details, material descriptions, dimensions of individual components and profiles, and finishes.

Door Hardware Schedule:  Prepared by or under the supervision of supplier, detailing fabrication and assembly of door hardware, as well as procedures and diagrams.  Coordinate the final Door Hardware Schedule with doors, frames, and related work to ensure proper size, thickness, hand, function, and finish of door hardware.

Format:  Comply with scheduling sequence and vertical format in DHI's "Sequence and Format for the Hardware Schedule."

Organization:  Organize the Door Hardware Schedule into door hardware sets indicating complete designations of every item required for each door or opening.

Organize door hardware sets in same order as in the Door Hardware Schedule at the end of Part 3.

Content:  Include the following information:

Type, style, function, size, label, hand, and finish of each door hardware item.

Manufacturer of each item.

Fastenings and other pertinent information.

Location of each door hardware set, cross-referenced to Drawings, both on floor plans and in door and frame schedule.

Explanation of abbreviations, symbols, and codes contained in schedule.

Mounting locations for door hardware.

Door and frame sizes and materials.

Submittal Sequence:  Submit the final Door Hardware Schedule at earliest possible date, particularly where approval of the Door Hardware Schedule must precede fabrication of other work that is critical in the Project construction schedule.  Include Product Data, Samples, Shop Drawings of other work affected by door hardware, and other information essential to the coordinated review of the Door Hardware Schedule.

Keying Schedule:  Prepared by or under the supervision of supplier, detailing the final keying instructions for locks.  Include schematic keying diagram and index each key set to unique door designations.

Product Certificates:  Signed by manufacturers of electrified door hardware certifying that products furnished comply with requirements.

Certify that door hardware approved for use on types and sizes of labeled fire doors complies with listed fire door assemblies.

Qualification Data:  For firms and persons specified in "Quality Assurance" Article.

Include lists of completed projects with project names and addresses of architects and owners, and other information specified.

Maintenance Data:  For each type of door hardware to include in maintenance manuals specified in Division 01.

Warranties:  Special warranties specified in this Section.

QUALITY ASSURANCE

Installer Qualifications:  An experienced installer who has completed door hardware similar in material, design, and extent to that indicated for this Project and whose work has resulted in construction with a record of successful in-service performance.

Supplier Qualifications:  Door hardware supplier with warehousing facilities in Project's vicinity and who is or employs a qualified Architectural Hardware Consultant, available during the course of the Work to consult with Contractor, Designer, and the Barnstable Public Facilities Project Manager about door hardware and keying.

Architectural Hardware Consultant Qualifications:  A person who is currently certified by the Door and Hardware Institute as an Architectural Hardware Consultant and who is experienced in providing consulting services for door hardware installations that are comparable in material, design, and extent to that indicated for this Project.

Source Limitations:  Obtain each type and variety of door hardware from a single manufacturer, unless otherwise indicated.

Regulatory Requirements:  Comply with provisions of the following:

Where indicated to comply with accessibility requirements, comply with Massachusetts Architectural Access Board and the Americans with Disabilities Act (ADA), "Accessibility Guidelines for Buildings and Facilities (ADAAG),"  as follows:

Handles, Pulls, Latches, Locks, and other Operating Devices:  Shape that is easy to grasp with one hand and does not require tight grasping, tight pinching, or twisting of the wrist.

Door Closers:  Comply with the following maximum opening-force requirements indicated:

Interior Hinged Doors:  5 lbf applied perpendicular to door.

Sliding or Folding Doors:  5 lbf applied parallel to door at latch.

Fire Doors:  Minimum opening force allowable by authorities having jurisdiction.

Thresholds:  Not more than 1/2 inch high.  Bevel raised thresholds with a slope of not more than 1:2.

NFPA 101:  Comply with the following for means of egress doors:

Latches, Locks, and Exit Devices:  Not more than 15 lbf to release the latch.  Locks shall not require the use of a key, tool, or special knowledge for operation.

Door Closers:  Not more than 30 lbf to set door in motion and not more than 15 lbf (67 N) to open door to minimum required width.

Thresholds:  Not more than 1/2 inch high.

Keying Conference:  Conduct conference at Project site to comply with requirements in Division 01.  Incorporate keying conference decisions into final keying schedule after reviewing door hardware keying system including, but not limited to, the following:

Function of building, flow of traffic, purpose of each area, degree of security required, and plans for future expansion.

Preliminary key system schematic diagram.

Requirements for key control system.

Address for delivery of keys.

Preinstallation Conference:  Conduct conference at Project site to comply with requirements in Division 01. Review methods and procedures related to electrified door hardware including, but not limited to, the following:

Review sequence of operation for each type of door hardware.

Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.

Review required testing, inspecting, and certifying procedures.

DELIVERY, STORAGE, AND HANDLING

Inventory door hardware on receipt and provide secure lock-up for door hardware delivered to Project site.

Tag each item or package separately with identification related to the final Door Hardware Schedule, and include basic installation instructions with each item or package.

Deliver keys to manufacturer of key control system.

COORDINATION

Templates:  Obtain and distribute to the parties involved templates for doors, frames, and other work specified to be factory prepared for installing door hardware.  Check Shop Drawings of other work to confirm that adequate provisions are made for locating and installing door hardware to comply with indicated requirements.

WARRANTY

General Warranty:  Special warranties specified in this Article shall not deprive the Town of Barnstable Project Manager of other rights the Town of Barnstable Project Manager may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

Special Warranty:  Written warranty, executed by manufacturer agreeing to repair or replace components of door hardware that fail in materials or workmanship within specified warranty period.  Failures include, but are not limited to, the following:

Structural failures including excessive deflection, cracking, or breakage.

Faulty operation of operators and door hardware.

Deterioration of metals, metal finishes, and other materials beyond normal weathering.

Warranty Period:  Three years from date of Substantial Completion, unless otherwise indicated.

Warranty Period for Manual Closers:  Ten years from date of Substantial Completion.

MAINTENANCE SERVICE

Maintenance Tools and Instructions:  Furnish a complete set of specialized tools and maintenance instructions as needed for the Middleborough Housing Authority continued adjustment, maintenance, and removal and replacement of door hardware.

PRODUCTS

SCHEDULED DOOR HARDWARE

Scheduled and acceptable manufacturers must provide all the functions and features of the specified product or it will not be approved.

| Item | Scheduled Manufacturer | Acceptable Manufacturers |
| --- | --- | --- |
| Hinges | Ives (IVE) | McKinney, Hager |
| Locksets & Deadlocks | Schlage (SCH) | Sargent, Best |
| Cylinders & Keying | Schlage (SCH) | User Standard |
| Door Closers & Auto Operators | LCN (LCN) | Norton |
| Push & Pull Plates & Bars | Ives (IVE) | Rockwood, Burns |
| Flush Bolts & Coordinators | Ives (IVE) | Rockwood, Burns |
| Protection Plates | Ives (IVE) | Rockwood, Burns |
| Stops & Holders | Ives (IVE) | Rockwood, Burns |
| Silencers | Ives (IVE) | Rockwood, Burns |
| Thresholds & Weatherstrip | National Guard (NGP) | Pemko, Reese |

Hand of Door:  Drawings show direction of slide, swing, or hand of each door leaf.  Furnish each item of hardware for proper installation and operation of door movement as shown.

Where the hardware specified is not adaptable to the finished shape or size of the members requiring hardware, furnish suitable types having the same operation and quality as the type specified, subject to the Architect's approval.

MATERIALS

Fasteners:

Provide hardware manufactured to conform to published templates, generally prepared for machine screw installation.

Furnish screws for installation with each hardware item.  Finish exposed (exposed under any condition) screws to match hardware finish, or, if exposed in surfaces of other work, to match finish of this other work as closely as possible including "prepared for paint" surfaces to receive painted finish.

Provide concealed fasteners for hardware units that are exposed when door is closed except to the extent that no standard units of type specified are available with concealed fasteners.  Do not use thru-bolts for installation where bolt head or nut on opposite face is exposed in other work unless their use is the only means of reinforcing the work adequately to fasten the hardware securely.

All hardware shall be installed with the fasteners provided by the hardware manufacturer.

Hinges:

The following is a guide for hinge type required for this specification:

1-3/4" thick doors up to and including 3'-0" wide:

Exterior:  standard weight, ball bearing, bronze/stainless steel, 4-1/2" high

Interior:  standard weight, ball bearing, steel, 4-1/2" high

1-3/4" thick doors over 3'-0" wide:

Exterior:  heavy weight, ball bearing, bronze/stainless steel, 5" high

Interior:  heavy weight, ball bearing, steel, 5" high

Provide 3 hinges per door leaf for doors 90 inches or less in height, and one additional hinge for each 30 inches of additional door height.

Hinge Pins:  Except as otherwise indicated, provide hinge pins as follows:

Steel Hinges:  Steel pins

Non-Ferrous Hinges:  Stainless steel pins

Out-Swinging Exterior Doors:  Non-removable pins

Interior Doors:  Non-rising pins

The width of hinges shall be 4-1/2" or as required for clearance.

Locksets shall be heavy-duty mortise lever type as manufactured by Schlage L-9000 Series. Handles to be lever handles grade 2L. Locks shall meet ANSI A-156.13 Series 1000, Grade 1 operational, Grade 1 security, Cylinder Schlage “Primus” 6-Pin tumbler C Keyway, 1 ¼" x 5 19/32" x 7/32" armored front, Strike: 1 1/8" x 3 5/8”, no lip with dust box Backset: 2 ¾"

Basisi of Design:  Schlage L 9000 series.  Other locks meeting this specification: Sargent 8200 Line series, Best 47H series.

Exit Devices:

Exit devices shall be touchpad type, fabricated of brass, bronze, stainless steel, or aluminum, plated to the standard architectural finishes to match the balance of the door hardware.

All exit devices shall incorporate a fluid damper or other device which eliminates noise associated with exit device operation.  Touchpad shall extend a minimum of one half of the door width.  End-cap will have two-point attachment to door.  Touch-pad shall match exit device finish, and shall be stainless steel for US32D finishes.  Only compression springs will be used in devices, latches, and outside trims or controls.

All devices to incorporate a security dead latching feature.

Provide roller strikes for all rim and surface mounted vertical rod devices, ASA strikes for mortise devices, and manufacturer's standard strikes for concealed vertical rod devices.

Mechanism case shall sit flush on the face of all flush doors, or spacers shall be furnished to fill gaps behind devices.  Where glass trim or molding projects off the face of the door, provide glass bead kits.

All non-fire-rated exit devices shall have cylinder dogging.

Where lever handles are specified as outside trim for exit devices, provide heavy-duty lever trims with forged or cast escutcheon plates.  Provide vandal-resistant levers that will travel to a 90-degree down position when more than 35 pounds of torque are applied, and which can easily be re-set.  Lever style will match the lever style of the locksets.

Exit devices shall be UL listed panic exit hardware.  All exit devices for fire rated openings shall be UL labeled fire exit hardware.

Provide electrical options as scheduled.

Exit devices meeting this specification:  Von Duprin 98 series, Precision Apex series, Sargent 80 series with dead latching.

Surface mounted, stainless steel (US32D finish), push pad device, top and bottom vertical rods and latches. UL listed for Panic Hardware; ANSI A156.3 – 2001 Grade 1.

Von Duprin 98/99 Series Surface Mounted Vertical Rod Device.

Models:

Right Hand Reverse Swing: 9827-L-NL-06-3’-US32D-RHR

Left Hand Reverse Swing: 9827-L-NL-06-3’-US32D-LHR

Options

CD – cylinder dogging as required by owner.

RG – rod guards at all bottom rods, surface mounted

Strikes shall coordinate with door frames and latching hardware.

Door Closers:

Door closers shall have fully hydraulic, full rack and pinion action with a high strength cast iron or cast aluminum cylinder.  Cylinder body shall be 1-1/2” in diameter, and double heat-treated pinion shall be 11/16” in diameter.

Hydraulic fluid shall be of a type requiring no seasonal closer adjustment for temperatures ranging from 120 degrees F to -30 degrees F.  Fluid shall be fireproof and shall pass the requirements of the UL10C “positive pressure” fire test.

Spring power shall be continuously adjustable over the full range of closer sizes, and allow for reduced opening force for the physically handicapped.  Hydraulic regulation shall be by tamper-proof, non-critical valves.  Closers shall have separate adjustment for latch speed, general speed, and back check.

All closers shall have solid forged steel main arms (and forged forearms for parallel arm closers).

Closers shall not incorporate a pressure relief valve.

All closers shall have metal covers.

Closer cylinders, arms, and metal covers shall have a powder coating finish which has been certified to exceed 100 hours salt spray testing by an independent testing laboratory used by BHMA for ANSI certification.  For metal components that can't be powder coated, a special rust inhibiting finish (SRI) must be used.

Door closers meeting this specification:  LCN 4040/4030 series, Norton 7500/PR7560 (standard screws).

Push Plates:  8" wide x 16" high x 0.050" thick.  Where door stile does not allow 8" wide plates, 4" wide plates may be used.

Door Pulls & Push Bars:  Solid bar stock, diameter and length as scheduled.  Push bars shall be of sufficient length to span from center to center of each stile.

Coordinators

Ives model COR9G or equivalent

Surface mounted, gravity type

Protection Plates:  Provide kick plates as scheduled, with 4 beveled edges.  Furnish with machine or wood screws, finished to match plates.  Plates shall be 8" high x 2" LWOD on single doors, 1" LWOD on pairs of doors.

Door Stops and Holders:

It shall be the responsibility of the hardware supplier to provide door stops for all doors in accordance with the following requirements:

Wall stops shall be used wherever possible.

Where wall stops cannot be used, provide dome type floor stops of the proper height.

At any opening where a wall or floor stop cannot be used, a heavy-duty overhead stop must be used.

Thresholds and Weatherstrip:  Furnish as scheduled and per architectural details.  Match finish of other items as closely as possible.  Provide only those units where resilient or flexible seal strip is easily replaceable and readily available.

National Guard

Nylon brush in aluminum channel.

Sizes necessary for full perimeter including door sweeps, jambs, heads and astragal.

Thresholds – National Guard or equal

Saddle Thresholds – 1/2 inch high x jamb width x door width

Model 424E with vinyl foot seal or equivalent

Silencers:  "Push-in" type silencers for each hollow metal or wood frame, 3 for each single frame, 2 for each pair frame.  Omit where gasketing is scheduled.

FINISHES

With the exception of all items listed below, the finish of all hardware shall be US26D - satin chrome or US32D - satin stainless steel.

Exceptions are as follows:

1.	Door Closers - aluminum powder coat finish.

2.	Coordinators - prime painted.

3.	Thresholds - mill finish aluminum.

4.	Weatherstrip & Sweeps - clear anodized aluminum.

5.	Silencers - grey.

KEYING

All locks and cylinders shall be construction master keyed and master keyed per the Owner’s instructions, to existing Everest/Primus key system.

All locks and cylinders, except cylinders for keypad locks will be interchangeable core type.

Provide 3 keys per lock, 6 construction master keys, and a total of 6 master keys for each group.

All master keys shall be delivered directly to the Owner by the hardware supplier, who shall obtain a receipt for delivery of same.

EXECUTION

EXAMINATION

Examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, labeled fire door assembly construction, wall and floor construction, and other conditions affecting performance.

Proceed with installation only after unsatisfactory conditions have been corrected.

PREPARATION

Steel Doors and Frames:  Comply with DHI A115 series.

Surface-Applied Door Hardware:  Drill and tap doors and frames according to SDI 107.

Wood Doors:  Comply with DHI A115-W series.

INSTALLATION

Mounting Heights:  Mount door hardware units at heights indicated in following applicable publications, unless specifically indicated or required to comply with governing regulations:

Standard Steel Doors and Frames:  DHI's "Recommended Locations for Architectural Hardware for Standard Steel Doors and Frames."

Custom Steel Doors and Frames:  DHI's "Recommended Locations for Builders' Hardware for Custom Steel Doors and Frames."

Wood Doors:  DHI WDHS.3, "Recommended Locations for Architectural Hardware for Wood Flush Doors."

Install each door hardware item to comply with manufacturer's written instructions.  Where cutting and fitting are required to install door hardware onto or into surfaces that are later to be painted or finished in another way, coordinate removal, storage, and reinstallation of surface protective trim units with finishing work.  Do not install surface-mounted items until finishes have been completed on substrates involved.

Set units level, plumb, and true to line and location.  Adjust and reinforce attachment substrates as necessary for proper installation and operation.

Drill and countersink units that are not factory prepared for anchorage fasteners.  Space fasteners and anchors according to industry standards.

Key Control System:  Place keys on markers and hooks in key control system cabinet, as determined by final keying schedule.

Boxed Power Supplies:  Locate power supplies as indicated or, if not indicated, above accessible ceilings. Verify location with Designer.

Configuration:  Provide the least number of power supplies required to adequately serve doors with electrified door hardware.

Thresholds:  Set thresholds for exterior and acoustical doors in full bed of sealant complying with requirements specified in Section 079200 - JOINT SEALANTS.

ADJUSTING

Initial Adjustment:  Adjust and check each operating item of door hardware and each door to ensure proper operation or function of every unit.  Replace units that cannot be adjusted to operate as intended.  Adjust door control devices to compensate for final operation of heating and ventilating equipment and to comply with referenced accessibility requirements.

Spring Hinges:  Adjust to achieve positive latching when door is allowed to close freely from an open position of 30 degrees.

Door Closers:  Adjust sweep period so that, from an open position of 70 degrees, the door will take at least 3 seconds to move to a point 3 inches from the latch, measured to the leading edge of the door.

Six-Month Adjustment:  Approximately six months after date of Substantial Completion, Installer shall perform the following:

Examine and readjust each item of door hardware as necessary to ensure function of doors, door hardware, and electrified door hardware.

Consult with and instruct the Town of Barnstable Project Manager's personnel on recommended maintenance procedures.

Replace door hardware items that have deteriorated or failed due to faulty design, materials, or installation of door hardware units.

CLEANING AND PROTECTION

Clean adjacent surfaces soiled by door hardware installation.

Clean operating items as necessary to restore proper function and finish.

Provide final protection and maintain conditions that ensure door hardware is without damage or deterioration at time of Substantial Completion.

Schedule

The following hardware sets are intended to establish type and standard of quality when used together with this section requirement. Examine Drawings and Specifications and furnish proper hardware for door openings.

Hardware Set A:  Classroom, Offices, Conference Room

Hinges:  Full mortise hinges as specified 11/2 pair.

LockMortise Lock, L9071/F09 Key Lock outside, inside always open with latch (ANSI F04) with mechanical lock.

Closer:  Surface mounted LCN 4030 as specified.

Kickplates:  10 inch high, both sides.

Door Stop:  Floor dome stop.

Hardware Set B:  Supply Closet (single) Locking

Hinges:  Full mortise hinges as specified 11/2 pair.

LockMortise Lock, L9080/F07, Key Lock outside, inside always open with latch (ANSI F04).

Kickplates:  10 inch high, both sides.

Holder	Surface mounted as specified.

Door Stop:	Floor dome stop.

Hardware Set C:  Staff Lavatories, Single

Hinges:  Full mortise hinges as specified 11/2 pair.

Lock:	Mortise lock, L9496/F15

Closer:	Surface mounted LCN 4030 as specified.

Kickplates:  10 inch high, both sides.

Door Stop:  Floor dome stop.

Hardware Set D:  Lavatories, Single

Hinges:  Full mortise hinges as specified 11/2 pair.

Lock:	Mortise Lock, L9010/F01 passage lock lever handle opens latch from either side.

Closer:	None

Kickplates:  10 inch high, both sides.

Door Stop:  Floor dome stop.

Hardware Set E:  Vestibule (pair) Non-Locking

Hinges:  Full mortise hinges as specified 11/2 pair each door.

Lock:  None

Pulls  Ives 8102-0

Push Plates:  Ives 8200

Kickplates:  10 inch high, pull side.

Closer:	Surface mounted LCN 4040 as specified.

Door Stop:	Floor dome stop.

Hardware Set F:  Exit Door Pairs

Hinges:  Full mortise hinges as specified 11/2 pair each door.

Latchset: Von Duprin specified or equal

Closer: surface mounted LCN 4040 as specified.

Lock:  coordinate keying with owner.

Strikes: sill and head, Von Duprin

Coordinators: Ives

Threshold: National Guard

Kickplates:  8 inch high, pull side.

Weatherstripping: National Guard; at all exterior doors

Door Stop: Wall stop at interior doors, floor stop at exterior doors

Hardware Set G:  Exit Door Pairs

Hinges:  Full mortise hinges as specified 11/2 pair.

Latchset: Von Duprin specified or equal

Closer: surface mounted LCN 4040 as specified.

Lock:  coordinate keying with owner.

Strikes: sill and head, Von Duprin

Threshold: National Guard

Kickplates:  8 inch high, pull side.

Weatherstripping: National Guard; at all exterior doors

Door Stop: Wall stop at interior doors, floor stop at exterior doors

.

END OF SECTION